## Disclaimer
Appendix 3 Interactive Model (Version 1.1)
Disclaimer: This model, including the choice of default input values, is based on our best scientific knowledge, professional judgements, and the information currently available. The model is for illustrative purposes only. It provides rough estimates of the reduction of relative infection risk due to long-range, airborne viral transmission, based on the inputs that a user enters in the tabs of "Simplified User Inputs" and "Other Default Inputs" and using simplified hypothetical scenarios. For details of model description, assumptions, and limitations, see the main document. Note that the formats of these interactive spreadsheets are slightly different from those described in the section of "Model Implementation" in the main document in order to be ADA-compliant. Update from Version 1.0 to 1.1: An "Outputs Particle Removal ACH" tab has been added. For detailed description, see Appendix F of the IAQ report entitled "Ventilation and Filtration to Reduce Long-range Airborne Transmission of COVID-19 and Other Respiratory Infections: Considerations for Reopened Schools."

## Outputs Particle Removal ACH
Model Outputs – Total Particle Removal ACH
Removal of Virus-containing Particles | Output | Units | Notes
due to outdoor air ventilation | 2.5398 | h-1 (or ACH) | Calculated based on the number of occupants, VR per person, and room volume. The number of occupants, ventilation rate per person, and room floor area are entered in "Simplified User Inputs." The room volume is calculated as floor area ´ height (which is set as 3 m in "Other Default Inputs" but users can change this input).
due to HVAC filter | 1.5992 | h-1 (or ACH) | Calculated based on the HVAC filter MERV rating and the recirculating airflow rate through the filter, assuming a constant total supply airflow rate of 6 ACH. The HVAC filter MERV rating is entered in "Simplified User Inputs." The 6 ACH total supply airflow rate is set in "Other Default Inputs" but users can change this input. The recirculating flow rate is then calculated as total supply airflow rate minus outdoor air VR.
due to portable air cleaner(s) | 1.8589 | h-1 (or ACH) | Calculated based on the total CADRs of selected portable air cleaners and room volume. The total CADRs and room floor area are entered in "Simplified User Inputs." The room volume is calculated as floor area times height (which is set as 3 m in "Other Default Inputs" but users can change this input).
Total | 5.9979 | h-1 (or ACH) | Total ACH = ACH due to outdoor air ventilation + HVAC filtration + portable air cleaner filtration; passive removal of particles (e.g., due to indoor surface deposition) are not summarized here but have been considered when calculating the relative infection risk.

## Outputs Relative Infection Risk
Model Outputs – Relative Infection Risk
Category | Output | Notes
Probability of infection for simulated case | 0.1378% | Probability of infection given current inputs in this file
Probability of infection for reference case | 0.1899% | Probability of infection given for the reference case The IAQ control measures for the reference case are: code-required minimum ventilation (VR = 7 L/s-person) + MERV 8 filter + No mask + No portable air cleaner. All other parameters used for the reference case are the same as those used for the simulated scenario case.
Relative infection risk (compared to the reference case) | 72.55% | Percent infection risk for simulated case compared to the reference case

## Simplified User Inputs
Simplified Model Inputs: Enter (or overwrite) values in the "User Input" column
Category | Parameter | User Input | Units | Note
Classroom size | Room floor area | 89.3 | m2 | Enter the floor area of the simulated classroom
Classroom occupancy | Room occupancy | 27 | person | Enter the number of occupants
Classroom occupancy | Exposure time | 5 | h | If not known, use school bell schedule
Classroom occupancy | Number of infected individuals | 1 | person | If not known, assume 1
Classroom occupancy | Total number of non-susceptible occupants (e.g., currently infected or immune due to previous recovery or vaccination) | 1 | person | If not known, assume same as the number of infected individuals
IAQ control measures - Source control | Consider wearing mask to reduce escape of virus-loaded particles from infected individuals? | 0 | n/a | Enter 1 if Yes; or 0 if No
IAQ control measures - Ventilation | VR per person | 7 | L/s-person | Enter the VR per person For example, the Title 24 code-required minimum outdoor air VRs for classrooms (age 9+) are 7 L/s-person (15 CFM/person) or 1.93 L/s-m2 (0.38 CFM/ft2), whichever is larger. If the VR is given in another format, convert it to equivalent per person VR first before entering.
IAQ control measures - HVAC filter | MERV rating | 8 | n/a | Enter 0 if no filter/filter rating; or enter 1–16 for MERV 1–16 filters
IAQ control measures - Portable air cleaner | CADR for tobacco smoke (0.09–1 μm) | 498 | m3/h | Enter 0 if no portable air cleaner; or enter total CADR in m3/h (i.e., the CADR for tobacco smoke, dust, and pollen as provided by the manufacturer ´ the total number of portable air cleaners in the classroom)
IAQ control measures - Portable air cleaner | CADR for dust (0.5–3 μm) | 498 | m3/h | (see note for tobacco smoke CADR)
IAQ control measures - Portable air cleaner | CADR for pollen (5–11 μm) | 498 | m3/h | (see note for tobacco smoke CADR)

## Other Default Inputs
Other inputs with detailed knowledge of building operations and airborne transmission: Enter (or overwrite) values in the "User Input" column
Category | Parameter | User Input | Units | Note
Classroom dimensions | Room height (H) | 3 | m | Default input value = 3 m
Occupant related | Pulmonary ventilation rate of a person | 0.5 | m3/h | Default input value = 0.5 m3/h
Occupant related | Quanta generation rate – Original | 1 | h-1 | Default input value = 1 h-1
Occupant related | Percentage reduction of quanta generation rate due to wearing mask | 50% | % | Default input value = 50%
Characteristics of the virus | Infectious particles in size bin 0.3–1 μm | 20% | % | Assume a total of 100% covering 0.3–10 μm Default input values = 20%, 30%, and 50% for infectious particles in size bins of 0.3–1 μm, 1–3 μm, and 3–10 μm, respectively
Characteristics of the virus | Infectious particles in size bin 1–3 μm | 30% | % | (see note for infectious particles in size bin 0.3–1 μm)
Characteristics of the virus | Infectious particles in size bin 3–10 μm | 50% | % | (see note for infectious particles in size bin 0.3–1 μm)
Characteristics of the virus | Infectious particles in size bin 0.09–1 μm | 20% | % | Assume a total of 100% covering 0.09–11 μm Default input values = 20%, 30%, and 50% for infectious particles in size bins of 0.09–1 μm, 0.5–3 μm, and 5–11 μm, respectively, used when evaluating the removal rate by portable air cleaner
Characteristics of the virus | Infectious particles in size bin 0.5–3 μm | 30% | % | (see note for infectious particles in size bin 0.09–1 μm)
Characteristics of the virus | Infectious particles in size bin 5–11 μm | 50% | % | (see note for infectious particles in size bin 0.09–1 μm)
Removal by ventilation and infiltration | Air change rate due to infiltration | 0.2 | h-1 | Default value = 0.2 h-1
Removal by surface deposition | Deposition rate for size bin 0.3–1 μm | 0.14 | h-1 | Assume the same particle size bins as those used for HVAC filter MERV ratings to simplify the calculation Default input values = 0.14 h-1, 0.29 h-1, and 0.91 h-1 for infectious particles in size bins of 0.31 μm, 1–3 μm, and 3–10 μm, respectively
Removal by surface deposition | Deposition rate for size bin 1–3 μm | 0.29 | h-1 | (see note for deposition rate for size bin 0.3–1 μm)
Removal by surface deposition | Deposition rate for size bin 3–10 μm | 0.91 | h-1 | (see note for deposition rate for size bin 0.3–1 μm)
Removal by HVAC filter | Total supply air flow (in ACH) | 6 | h-1 | Default input value = 6 ACH
Removal by HVAC filter | Fractional operation time of HVAC system | 100% | % | Default input value = 100%

## Other Calculations
Model calculations based on users inputs and simplified MERV table
Category | Parameter | Model Calculated Value | Units | Note
Classroom dimensions | Room volume (V) | 267.9 | m3 | Calculated from User Inputs and Default Inputs
Occupant related | Number of susceptible individuals | 26 | person | Calculated from User Inputs
Occupant related | Quanta generation rate – including effect of mask wearing | 1 | h-1 | Calculated from User Inputs and Default Inputs
Removal by ventilation and infiltration | Ventilation rate (Q_ventilation) | 680.4 | m3/h | Calculated from User Inputs
Removal by ventilation and infiltration | Air change rate due to ventilation | 2.5398 | h-1 | Calculated from VR and Room Volume
Removal by ventilation and infiltration | Infiltration rate (Q_infiltration) | 53.58 | m3/h | Calculated from Default Inputs and Room Volume
Removal by ventilation and infiltration | Sum of ventilation and infiltration rate | 733.98 | m3/h | Calculated from VR and Infiltration Rate
Removal by ventilation and infiltration | Air change rate due to ventilation + infiltration | 2.7398 | 1/h | Calculated from sum of VR/Infiltration Rate and Room Volume
Removal by surface deposition | Combined deposition removal rate for infectious particles | 0.57 | h-1 | Calculated from Default Inputs
Removal by HVAC filter | Total supply air flow rate | 1607.4 | m3/h | Calculated from Default Inputs
Removal by HVAC filter | Fraction of recirculated air in the total supply airflow | 0.57671 | % | Calculated from VR and Total supply air flow rate
Removal by HVAC filter | Filtration efficiency for size bin 0.3–1 μm | 0.14833 | % | Automatically linked to "Simplified MERV Table" using the filter MERV rating that a user enters in "Simplified User Inputs"
Removal by HVAC filter | Filtration efficiency for size bin 1–3 μm | 0.275 | % | (see note for filtration efficiency for size bin 0.3–1 μm)
Removal by HVAC filter | Filtration efficiency for size bin 3–10 μm | 0.7 | % | (see note for filtration efficiency for size bin 0.3–1 μm)
Removal by HVAC filter | Filtration removal rate for size bin 0.3–1 μm | 0.51327 | h-1 | Calculated as the product of recirculated airflow rate, filter efficiency, and the fractional operation time of HVAC system, assuming average indoor concentration of infectious particles in the recirculated air entering the filter
Removal by HVAC filter | Filtration removal rate for size bin 1–3 μm | 0.95157 | h-1 | (see note for filtration removal rate for size bin 0.3–1 μm)
Removal by HVAC filter | Filtration removal rate for size bin 3–10 μm | 2.4222 | h-1 | (see note for filtration removal rate for size bin 0.3–1 μm)
Removal by HVAC filter | Combined HVAC filter removal rate for infectious particles | 1.5992 | h-1 | Calculated from Filtration removal rates for the three size bins
Removal by portable (in-room) air cleaner | Air cleaner removal rate for size bin 0.09–1 μm | 1.8589 | h-1 | Calculated based on the CADRs that a user enters in "Simplified User Inputs," assuming portable air cleaner(s) run continuously when the classroom is occupied
Removal by portable (in-room) air cleaner | Air cleaner removal rate for size bin 0.5–3 μm | 1.8589 | h-1 | (see note for air cleaner removal rate for size bin 0.09–1 μm)
Removal by portable (in-room) air cleaner | Air cleaner removal rate for size bin 5–11 μm | 1.8589 | h-1 | (see note for air cleaner removal rate for size bin 0.09–1 μm)
Removal by portable (in-room) air cleaner | Combined portable air cleaner removal rate for infectious particles | 1.8589 | h-1 | Calculated from air cleaner removal rates for the three size bins

## Simplified MERV Table
Simplified MERV Table
MERV Rating | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Filtration efficiency (%) for size bin 0.3–1 μm | 0% | 0% | 0% | 0% | 0% | 1.833% | 1.833% | 14.83% | 14.83% | 14.83% | 14.83% | 19.33% | 19.33% | 65% | 75% | 85% | 95%
Filtration efficiency (%) for size bin 1–3 μm | 0% | 0% | 0% | 0% | 0% | 8.333% | 8.333% | 27.5% | 27.5% | 40% | 50% | 65% | 80% | 90% | 90% | 90% | 95%
Filtration efficiency (%) for size bin 3–10 μm | 0% | 10% | 10% | 10% | 10% | 20% | 35% | 50% | 70% | 85% | 85% | 85% | 90% | 90% | 90% | 90% | 95%
Note: ASHRAE 52.2-2017 Table J-2 was used first. To be conservative, we used the lower bound of the minimum, composite, average particle size removal efficiencies specified in ASHRAE 52.2 Table J-2 (i.e., apply to MERV 14–16 filters for 0.3–1 μm particles, MERV 10–16 filters for 1–3 μm particles, and MERV 5–16 filters for 3–10 μm particles). We also assumed a filtration efficiency of 65% for MERV 13 for 0.3–1 μm particles, 40% for MERV 9 for 1–3 μm particles, and 10% for MERV 1–4 filters for 3–10 μm particles. For low MERV-rating filters that do not have removal efficiencies specified in ASHRAE 52.2 Table J-2 (i.e., MERV 1–12 filters for 0.3–1 μm particles, and MERV 1–8 filters for 1–3 μm particles), we used the 50th percentile of the cumulative filtration efficiency distributions (P50%) from Dillon and Sextro (2020) and further divided them by a factor of three to make a conservative estimate. For filters of MERV 1–12, we used the average of P50% for 0.3 and 1 μm - for particles in the size range of 0.3–1 μm. For filters of MERV 1–8, we used the average of P50% for 1 and 3 μm for particles of 1–3 μm. If P50% was not given for a specific MERV rating filter (i.e., MERV 1–4, 6, 9 and 10), we used the value for the closest lower MERV-rating filter.

## Data Source for MERV Table
Data source: ASHRAE 52.2-2017 Table J-2 & Table 10 from Dillon and Sextro (2020)
MERV Rating | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Filtration efficiency (%) for 0.1 μm | 0% | Blank | Blank | Blank | Blank | 1% | Blank | 20% | 20% | Blank | Blank | 40% | 40% | Blank | 86% | 86% | Blank
Filtration efficiency (%) for 0.3 μm | 0% | Blank | Blank | Blank | Blank | 1% | Blank | 20% | 20% | Blank | Blank | 40% | 40% | Blank | 86% | 86% | Blank
Filtration efficiency (%) for 1 μm | 0% | Blank | Blank | Blank | Blank | 10% | Blank | 69% | 69% | Blank | Blank | 76% | 76% | Blank | 98% | 98% | Blank
Filtration efficiency (%) for 3 μm | 0% | Blank | Blank | Blank | Blank | 40% | Blank | 96% | 96% | Blank | Blank | 95% | 95% | Blank | 100% | 100% | Blank
Filtration efficiency (%) for 10 μm | 0% | Blank | Blank | Blank | Blank | 45% | Blank | 99% | 99% | Blank | Blank | 98% | 98% | Blank | 100% | 100% | Blank
ASHRAE 52.2-2017 Table J-2, Standard 52.2: Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size. 2017, American Society of Heating, Refrigerating, and Air-Conditioning Engineers: Atlanta, GA.
Dillon, M.B. and R.G. Sextro, Reducing Exposures to Airborne Particles Through Improved Filtration: A High-Level Modeling Analysis. medRxiv, 2020.

## Reference Case Definition
Reference Case: Code-required minimum VR + MERV 8 filter + No mask + No portable air cleaner
Category | Parameter | Value Used for Reference Case | Units | Note
Classroom dimensions | Room height (H) | 3 | m | Default input taken from the simulated case
Classroom dimensions | Room volume (V) | 267.9 | m3 | Calculated from User Inputs and Default Inputs taken from the simulated case
Occupant related | Pulmonary ventilation rate of a person | 0.5 | m3/h | Default input taken from the simulated case
Occupant related | Number of susceptible individuals | 26 | person | User input taken from the simulated case
Occupant related | Quanta generation rate – Original | 1 | h-1 | Default input taken from the simulated case
Occupant related | Percentage reduction of quanta generation rate due to wearing mask | 0% | not applicable | Assume no mask-wearing for the reference case
Occupant related | Quanta generation rate – including effect of wearing mask | 1 | h-1 | Calculated from User Inputs and Default Inputs taken from the simulated case
Characteristics of the virus | Infectious particles in size bin of 0.3–1 μm | 20% | % | Default input taken from the simulated case
Characteristics of the virus | Infectious particles in size bin of 1–3 μm | 30% | % | Default input taken from the simulated case
Characteristics of the virus | Infectious particles in size bin of 3–10 μm | 50% | % | Default input taken from the simulated case
Characteristics of the virus | Infectious particles in size bin of 0.09–1 μm | 20% | % | Default input taken from the simulated case
Characteristics of the virus | Infectious particles in size bin of 0.5–3 μm | 30% | % | Default input taken from the simulated case
Characteristics of the virus | Infectious particles in size bin of 5–11 μm | 50% | % | Default input taken from the simulated case
Removal by ventilation and infiltration | Ventilation rate (Q_ventilation) – Final | 680.4 | m3/h | Assume VR = 7 L/s-person (Title 24 code required minimum for the classroom defined) for the reference case
Removal by ventilation and infiltration | Air change rate due to ventilation | 2.5398 | h-1 | Calculated from VR and Room Volume
Removal by ventilation and infiltration | Infiltration rate (Q_infiltration) | 53.58 | m3/h | Calculated from air change rate due to infiltration and Room Volume
Removal by ventilation and infiltration | Air change rate due to infiltration | 0.2 | h-1 | Default input taken from the simulated case
Removal by ventilation and infiltration | Sum of ventilation and infiltration rate | 733.98 | m3/h | Calculated from VR and Infiltration Rate
Removal by ventilation and infiltration | Air change rate due to ventilation + infiltration | 2.7398 | 1/h | Calculated from sum of VR/Infiltration Rate and Room Volume
Removal by surface deposition | Deposition rate for size bin of 0.3–1 μm | 0.14 | h-1 | Default input taken from the simulated case
Removal by surface deposition | Deposition rate for size bin of 1–3 μm | 0.29 | h-1 | Default input taken from the simulated case
Removal by surface deposition | Deposition rate for size bin of 3–10 μm | 0.91 | h-1 | Default input taken from the simulated case
Removal by surface deposition | Combined deposition removal rate for infectious particles | 0.57 | h-1 | Calculated from Default Inputs taken from the simulated case
Removal by HVAC filter | Total supply air flow (in ACH) | 6 | h-1 | Default input taken from the simulated case
Removal by HVAC filter | Fractional operation time of HVAC system | 100% | % | Default input taken from the simulated case
Removal by HVAC filter | Total supply air flow rate | 1607.4 | m3/h | Calculated from Default Inputs taken from the simulated case
Removal by HVAC filter | Fraction of recirculated air in the total supply airflow | 57.67% | % | Calculated from VR and Total supply air flow rate
Removal by HVAC filter | Filtration efficiency for size bin of 0.3–1 μm | 14.83% | % | Assume MERV 8 HVAC filter for the reference case
Removal by HVAC filter | Filtration efficiency for size bin of 1–3 μm | 27.5% | % | (see note for filtration efficiency for size bin 0.3-1 μm)
Removal by HVAC filter | Filtration efficiency for size bin of 3–10 μm | 70% | % | (see note for filtration efficiency for size bin 0.3-1 μm)
Removal by HVAC filter | Filtration removal rate for size bin of 0.3–1 μm | 0.51327 | h-1 | Calculated as the product of recirculated airflow rate, filter efficiency, and the fractional operation time of HVAC system, assuming average indoor concentration of infectious particles in the recirculated air entering the filter
Removal by HVAC filter | Filtration removal rate for size bin of 1–3 μm | 0.95157 | h-1 | (see note for filtration removal efficiency rate for size bin 0.3-1 μm)
Removal by HVAC filter | Filtration removal rate for size bin of 3–10 μm | 2.4222 | h-1 | (see note for filtration removal efficiency rate for size bin 0.3-1 μm)
Removal by HVAC filter | Combined HVAC filter removal rate for infectious particles | 1.5992 | h-1 | Calculated from Filtration removal rates for the three size bins
Removal by portable (in-room) air cleaner | Air cleaner removal rate for size bin of 0.09–1 μm | 0 | h-1 | Assume no portable air cleaner for the reference case
Removal by portable (in-room) air cleaner | Air cleaner removal rate for size bin of 0.5–3 μm | 0 | h-1 | (see note for air cleaner removal rate for size bin 0.09-1 μm)
Removal by portable (in-room) air cleaner | Air cleaner removal rate for size bin of 5–11 μm | 0 | h-1 | (see note for air cleaner removal rate for size bin 0.09-1 μm)
Removal by portable (in-room) air cleaner | Combined portable air cleaner removal rate for infectious particles | 0 | h-1 | Calculated from air cleaner removal rates for the three size bins