## Disclaimer
Classroom CO2 Decay Measurement and Ventilation Rate Calculation Datasheet (using International System of Units [SI] units)
Disclaimer: This spreadsheet is for illustrative purposes only. It demonstrates how to estimate outdoor air ventilation rates (VRs) based on classroom CO2 decay measurement. For details of how to conduct a CO2 decay test, see Appendix E of the IAQ report entitled "Ventilation and Filtration to Reduce Long-range Airborne Transmission of COVID-19 and Other Respiratory Infections: Considerations for Reopened Schools".

## Example datasheet
Information to be entered by field inspector: Blue – User inputs (Example)
Inspector's name: | Jane Jones | Date: | 2021-01-21
Category | Parameter | User input | Units | Note
Classroom information | Classroom name | 101 | n/a | Enter classroom name or number
Classroom information | Floor area | 89.2 | m2 | Measure and enter floor area
Classroom information | Ceiling height | 2.7 | m | Measure and enter average ceiling height
Classroom information | Number occupants | 27 | person | Enter expected maximum number occupants
CO2 monitor reading | Coutdoor initial | 433 | ppm | Enter initial outdoor CO2 concentration; if not measured, assume 400 ppm
Measurement time | T1 | 10:14 | h:min | Enter time Coutdoor initial measured
CO2 monitor reading | Cindoor initial | 1063 | ppm | Enter initial indoor CO2 concentration
Measurement time | T2 | 10:37 | h:min | Enter time Cindoor initial measured
CO2 monitor reading | Cindoor final | 546 | ppm | Enter final indoor CO2 concentration
Measurement time | T3 | 11:07 | h:min | Enter time Cindoor final measured
CO2 monitor reading | Coutdoor final | 449 | ppm | Enter final outdoor CO2 concentration; if not measured, assume 400 ppm
Measurement time | T4 | 11:23 | h:min | Enter time Coutdoor final measured

## Example calculations
Calculated Values based on Example Datasheet (Example)
Category | Parameter | Calculated value | Units | Note
Classroom information | Volume | 240.84 | m3 | Calculated as (Floor area ´ Ceiling height)
CO2 concentration | Coutdoor average | 441 | ppm | Calculated as average of Coutdoor initial and Coutdoor final
CO2 concentration | Cindoor initial − Coutdoor average | 622 | ppm | Initial indoor concentration after background subtraction
CO2 concentration | Cindoor final − Coutdoor average | 105 | ppm | Final indoor concentration after background subtraction
CO2 concentration | (Cindoor final − Coutdoor average)/ (Cindoor initial − Coutdoor average) | 0.16881 | unitless | Ratio of corrected final to initial indoor concentration
Measurement time | T3 – T2 | 30 | min | Time used for VR calculation

## Example estimated VR
Estimated VR: Red – Model Outputs (Example)
Category | Parameter | Calculated value | Units
Estimated VR | Outdoor air change rate (ACH) | 3.558 | h-1 (or ACH)
Estimated VR | Outdoor airflow rate | 856.899 | m3/h
Estimated VR | Outdoor airflow rate per occupant | 8.8158 | L/s-occupant
Estimated VR | Outdoor airflow rate per floor area | 2.3567 | L/s-m2

## Blank datasheet
Information to be entered by field inspector: Blue – User inputs (Blank datasheet)
Inspector's name: |  | Date:
Category | Parameter | User input | Units | Note
Classroom information | Classroom name | no data | n/a | Enter classroom name or number
Classroom information | Floor area | no data | m2 | Measure and enter floor area
Classroom information | Ceiling height | no data | m | Measure and enter average ceiling height
Classroom information | Number occupants | no data | person | Enter expected maximum number occupants
CO2 monitor reading | Coutdoor initial | no data | ppm | Enter initial outdoor CO2 concentration; if not measured, assume 400 ppm
Measurement time | T1 | no data | h:min | Enter time Coutdoor initial measured
CO2 monitor reading | Cindoor initial | no data | ppm | Enter initial indoor CO2 concentration
Measurement time | T2 | no data | h:min | Enter time Cindoor initial measured
CO2 monitor reading | Cindoor final | no data | ppm | Enter final indoor CO2 concentration
Measurement time | T3 | no data | h:min | Enter time Cindoor final measured
CO2 monitor reading | Coutdoor final | no data | ppm | Enter final outdoor CO2 concentration; if not measured, assume 400 ppm
Measurement time | T4 | no data | h:min | Enter time Coutdoor final measured

## Blank calculations
Calculated Values based on Blank Datasheet
Category | Parameter | Calculated value | Units | Note
Classroom information | Volume | #VALUE! | m3 | Calculated as (Floor area ´ Ceiling height)
CO2 concentration | Coutdoor average | #DIV/0! | ppm | Calculated as average of Coutdoor initial and Coutdoor final
CO2 concentration | Cindoor initial − Coutdoor average | #VALUE! | ppm | Initial indoor concentration after background subtraction
CO2 concentration | Cindoor final − Coutdoor average | #VALUE! | ppm | Final indoor concentration after background subtraction
CO2 concentration | (Cindoor final − Coutdoor average)/ (Cindoor initial − Coutdoor average) | #VALUE! | unitless | Ratio of corrected final to initial indoor concentration
Measurement time | T3 – T2 | #VALUE! | min | Time used for VR calculation

## Blank estimated VR
Estimated VR: Red – Model Outputs
Category | Parameter | Calculated value | Units
Estimated VR | Outdoor air change rate (ACH) | #VALUE! | h-1 (or ACH)
Estimated VR | Outdoor airflow rate | #VALUE! | m3/h
Estimated VR | Outdoor airflow rate per occupant | #VALUE! | L/s-occupant
Estimated VR | Outdoor airflow rate per floor area | #VALUE! | L/s-m2