## Disclaimer
Classroom Window Openable Area Inspection Datasheet (using International System of Units [SI] units)
Disclaimer: This spreadsheet is for illustrative purposes only based on the inputs that a user enters in the tab of "Example datasheet". It demonstrates how to estimate total openable area of windows. For details of how to conduct DIY inspection for the area of openable windows in classrooms, see Appendix B of the IAQ report entitled "Ventilation and Filtration to Reduce Long-range Airborne Transmission of COVID-19 and Other Respiratory Infections: Considerations for Reopened Schools."

## Example datasheet
Information to be entered by field inspector (or user) : Enter (or overwrite) values in the columns of "User Input 1", "User Input 2", "User Input 3", "User Input 4", and "User Input 5", and in cells B2, D2 and F2
Inspector's name: | Jane Jones | Date: | 2021-01-21 | Classroom Name: | 101
User Input 1: Room Floor Area | Units (floor area) | User Input 2: Window Number | User Input 3: Is window obstructed? (Yes or No) | User Input 4: Window Width or Swing-open Distance | Units (input 4) | User Input 5: Window Height or Swing-open Distance | Units (input 5) | Note
89.2 | m2 | 1 | No | 91 | cm | 86 | cm | If the window is unobstructed, enter "No" for "User Input 3." If the window is obstructed and cannot open, enter "Yes" for "User Input 3" and then "0" for both "User Input 4" and "User Input 5."
Blank | Blank | 2 | No | 91 | cm | 84 | cm | (see note for window 1)
Blank | Blank | 3 | No | 91 | cm | 81 | cm | (see note for window 1)
Blank | Blank | 4 | No | 91 | cm | 84 | cm | (see note for window 1)
Blank | Blank | 5 | No | 91 | cm | 86 | cm | (see note for window 1)
Blank | Blank | 6 | No | 91 | cm | 86 | cm | (see note for window 1)
Blank | Blank | 7 | Yes | 0 | cm | 0 | cm | (see note for window 1)

## Example calculations
Calculated Values based on Example Datasheet
Window Number | Openable Window Area | Units | Note
1 | 0.7826 | m2 | Openable area for each window is calculated as "Width or Swing-open Distance" × "Height or Swing-open Distance"
2 | 0.7644 | m2 | (see note for window 1)
3 | 0.7371 | m2 | (see note for window 1)
4 | 0.7644 | m2 | (see note for window 1)
5 | 0.7826 | m2 | (see note for window 1)
6 | 0.7826 | m2 | (see note for window 1)
7 | 0 | m2 | (see note for window 1)

## Example outputs-total win area
Estimated percentage of total openable window area to floor area: Model Outputs
Output Parameter | Calculated Value | Units
Total openable area for unobstructed windows | 4.6137 | m2
Total window openable area as a percentage of floor area | 5.172% | unitless
Note: Title 24 requires that classrooms have windows with a total openable area of at least four percent of the floor area or a mechanical ventilation system with an outdoor air VR of at least 15 cfm/occupant or 0.15 cfm/ft2, whichever is greater | Blank | Blank